Efficient Generation: Combustion Turbine Electric Generating Units

Technical Support Document

New Source Performance Standards for Greenhouse Gas Emissions from New, Modified, and Reconstructed Fossil Fuel-Fired Electric Generating Units; Emissions Guidelines for Greenhouse Gas Emissions from Existing Fossil Fuel-Fired Electric Generating Units; and Repeal of the Affordable Clean Energy Rule Proposal

Docket ID No. EPA-HQ-OAR-2023-0072

U.S. Environmental Protection Agency

Office of Air and Radiation

March 2023

Table of Contents

Introduction	3

Potential Efficiency Gains at Simple Cycle EGUs	3

Steam Injection	4

Pressure Gain Combustion	6

Potential Efficiency Gains in Combined Cycle EGUs	7

Advances in Combined Cycle Operation	7

HRSG Configurations	9

Potential Efficiency Gains in the Bottoming (Rankine) Cycle	11

Heat Recovery Steam Generation Design Optimization	12

Intercooled Combined Cycle	13

Blowdown Heat Recovery	14

Design and Operating and Maintenance Practices	14

Once Through (Benson®) HRSG Technology	16

The Use of Supercritical Steam Conditions	17

The Use of Alternate Working Fluid	19

The Use of Thermoelectric Materials	21

Combined Cycle Start-up Times	22

Purge Credit	25

# Introduction

This technical support document describes the factors that impact the efficiency of both simple and combined cycle combustion turbines. It describes designs and operation and maintenance practices that can improve the efficiency of combustion turbines, which reduces fuel use and emissions of greenhouse gases.

As the thermal efficiency of a combustion turbine increases, less fuel is burned per gross megawatt of electricity produced by the turbine-generator and there is a corresponding decrease in carbon dioxide (CO2) and other air emissions. Efficiency is reported as the percentage of the energy in the fuel that is converted to electricity. Heat rate is another common way to express efficiency. Heat rate is expressed as the number of British thermal units (Btu) or kilojoules (kJ) required to generate a kilowatt (kWh) of electricity. Lower heat rates are associated with more efficient power generation. Efficiency improvements can be expressed in different formats; they may be reported as an absolute change in overall efficiency (e.g., a change from 40% to 42% represents a 2% absolute increase). They may also be presented as the relative change in efficiency (e.g., a change from 40% to 42% is a relative change in efficiency and fuel use of 5%). The relative change in efficiency is the most consistent approach, since it corresponds to the same change in heat rate. For combustion turbine EGUs as a whole, as heat rates are reduced there are also reductions in fuel extraction related environmental impacts and in any associated thermal impacts on cooling water eco-systems.

The electric energy output for an EGU can be expressed as either “gross output” or “net output.” The gross output of an EGU is the total amount of electricity generated at the generator terminal. The net output of an EGU is the gross output minus the total amount of auxiliary (i.e., parasitic) electricity used to operate the EGU (e.g., electricity to power fuel handling equipment, pumps, fans, pollution control equipment, and other on-site electricity needs), and thus is a measure of the electricity delivered to the transmission grid for distribution and sale to customers.

Multiple design and operation and maintenance parameters influence the efficiency of a combustion turbine EGU. The following is a brief summary of some of the design parameters that impact the CO2 emission rate of combustion turbine EGUs. This summary is not intended to be a comprehensive list of all design parameters that influence the CO2 emission rate.

Combined cycle (CC) electricity generating units (EGUs) are power plants using both a combustion turbine engine (topping or Brayton cycle) and a steam turbine (bottoming or Rankine cycle) to generate electricity. Fuel is first burned in a combustion turbine engine, and the exhaust heat from the combustion turbine engine is recovered by a heat recovery steam generator (HRSG) to generate useful thermal output (e.g., steam). The steam is then used as the working fluid in a Rankine cycle and expanded through a turbine to generate additional power. Combined cycles have significantly higher efficiencies compared to simple cycle combustion turbines—combustion turbine engines where the energy in the turbine exhaust is not recovered for a useful purpose.

# Potential Efficiency Gains at Simple Cycle EGUs

Simple cycle design has been iterated over the years to improve simple cycle efficiency, to increase capacity, and to reduce emissions. Efficiency improvements include increased firing temperatures, increasing compression rations, and the addition of intercooling. According to Gas Turbine world, the design net efficiency of simple cycle turbines range from 32 to 40%. These are design efficiencies at specified conditions, and both power output and efficiency are impacted by ambient conditions. In general, efficiency and output tend to decrease at higher ambient temperatures and increase at lower ambient temperatures. Several approaches are available to address both the loss in output and efficiency at higher ambient temperatures.

Efficiency and output of combustion turbines degrade as ambient temperatures increase. More specifically, ambient temperature is believed to reduce power output by 2.5% for every 10oF above 59oF. To reduce the impacts of elevated ambient temperatures on simple cycle combustion turbines, owners/operators employ inlet air cooling techniques that generally fall in to two categories: evaporative cooling and chilling systems. Evaporative cooling works by adding liquid water to the combustion air. As the water evaporates, it cools the combustion air. Chilling systems use mechanical or adsorption chillers to reduce combustion air temperature.  One common type of cooling is inlet fogging, an evaporative cooling system. Inlet fogging works by spraying fine (typically < 20 microns) water particles into the inlet combustion turbine air, leading to lower inlet air temperatures and higher efficiencies.  A system like inlet fogging, but resulting in higher efficiency, is wet compression. Wet compression works by spraying an excess of fog into the inlet air, so that fog still exists after the air is fully saturated. Some of the excess fog droplets are not evaporated until they are carried into the compressor, which provides additional cooling. This results in further power increases of the combustion turbine engine.

GE has its own intercooling technology, which it refers to as “SPRINT”, or “SPray INTercooling”. The SPRINT technology is paired with a LM6000 combustion turbine to its combustion air. More specially, demineralized water is atomized with high-pressure compressed air and sprayed into the inlet of the low-pressure compressor and high-pressure compressor. This results in a higher mass flow through the compressor and increased power output. Moreover, this technology can result in high incremental output and improved efficiency as ambient temperatures rise. The design output and efficiencies for three different LM6000 combustion turbines with and without SPRINT technology are outlined in Figure 1.

Figure 1: Comparison of LM6000 Combustion Turbines With and Without SPRINT Technology

| Gas Turbine | ISO Base Load (MW) | Efficiency (%) |
| --- | --- | --- |
| LM6000 PC | 46.6 | 40.0% |
| LM6000 PC Sprint | 51.1 | 39.8% |
| LM6000 PG | 56 | 39.1% |
| LM6000 PG Sprint | 57.2 | 38.7% |
| LM6000 PF | 44.7 | 41.4% |
| LM6000 PF Sprint | 50.0 | 41.4% |

Water injection is a process by which water is injected into the combustor and provides NOx control. NOx emissions from the combustor have been shown to increase exponentially with increasing temperatures. Thus, water injected into the combustor flame area to lower the temperature and, consequently, reduce NOx emissions. Water injection is believed to result in a 60-80% reduction of NOx emissions. Additionally, experimental results have shown that water and steam injections can lower exhaust gas temperatures to reduce NOx emissions by 70% and 57%, respectively.

## Steam Injection

Steam inject is similar to water injection, except that steam, instead of liquid water, is injected into the combustion chamber. The advantage of steam injection is that it improves the efficiency and increases the output of the combustion turbine as well as reducing NOX emissions. Multiple vendors offer different variations of steam injection. The basic process is the use of a relatively low cost HRSG to produce steam. Instead of recovering the energy by expanding the steam through a steam turbine, the steam is injected into the combustion chamber of the combustion turbine and the energy is extracted by the combustion turbine engine itself. Combustion turbines using steam injection have characteristics in-between simple cycle and combined cycle combustion turbines. They are more efficient, but more complex and have higher capital costs than simple cycle combustion turbines without steam injection. Combustion turbines using steam injection and simpler and have lower capital costs than combined EGUs but have lower efficiencies.

A steam injection gas turbine cycle (STIG) is to the steam injection process used in GE combustion turbines. For STIG cycles, the steam source is specifically provided by the HRSG to increase both cycle efficiency and power output. One study modeled the performance of a GE Frame 6b simple cycle that was retrofitted with a STIG cycle, and results suggest that efficiency can be increased from 30% to 40% and that power output can be increased from 38 to 50 MW. The relative improvements suggested by this study are similar to estimates from GE. GE advertises that its LM2500 aeroderivative combustion turbine can have an improved power output by 25% when outfitted with a STIG cycle.  STIG uses constant pressure HRSG and operation is limited to near full load when thermal load is relatively constant. The exhaust temperature drops at partial loads and the HRSG cannot maintain a balanced heat transfer. While combined cycle EGUs have higher efficiencies than the STIG cycle, the STIG cycle is simpler and requires less capital.

Mitsubishi Power’s Smart-AHAT (Advanced Humid Air Turbine) is a steam injection system that achieves near zero water make-up using an integrated water recovery system. The system is potentially less complex and more flexible than combined cycle systems, with efficiencies significantly higher than conventional simple cycle plants. The HRSG involved in the system is a conventional single-pressure unit that produces the steam required for the combustion turbine steam injection. An important benefit of the Smart-AHAT system is water preservation. Without a water recovery system (WRS), water in the form of steam would exit the system through the HRSG stack leading to large amounts of water lost to the atmosphere. Smart-AHAT uses a direct, spray-type heat exchanger to reduce the HRSG exhaust gas temperature below the water dew point of the flue gas and cause condensation of the water vapor. Some condensate is recirculated to the spray nozzles of the heat exchange, while the rest if treated and returned as feed water for the HRSG steam production. Other benefits include reduced NOX emissions and shorter construction cycles and lower costs than combined cycle plants.

The Cheng Cycle provides more flexibility by using a variable pressure HRSG and the operating range is from idle to full load. This approach provides the optimal heat recovery and steam injection capacity at a range of loads. Original performance measurements indicated the implementing a Cheng Cycle system on a combustion turbine can provide up to a 26% efficiency improvement compared to the base turbine engine.

## Pressure Gain Combustion

Pressure gain combustion (PGC) has the potential to increase combustion turbine power plant efficiency and reduce emissions. Estimates for higher efficiencies could reach 4-6% for simple cycle systems and 2-4% in combined cycle systems. In conventional combustion turbines, engines undergo steady, subsonic combustion which results in a total pressure loss. In PGC, multiple physical phenomena such as resonant pulsed combustion, constant volume combustion, and detonation can be used to create a rise in effective pressure across the combustor while consuming an equal quantity of fuel. The DOE assessed the inclusion of PGC in combined cycle power plants. The study found that a PGC integrated system produced 3.09% more power at the same fuel flow rate and reduced the cost of electricity (COE) by 0.58%. One key advantage of PGC technology is that it can be compounded with other combustion turbine technology improvements such as compressor efficiency. Applications of PGC hold promise towards the Advanced Turbine Program’s efficiency goals. DOE’s integrated PGC system achieved a net LHV efficiency of 64.56%, while a PGC system that included other combustion turbine technology improvements achieved a LHV efficiency of 66.68%.

# Potential Efficiency Gains in Combined Cycle EGUs

## Advances in Combined Cycle Operation

While many configurations of HRSGs are available to improve the steam bottoming cycle efficiency, several improvements have been made to other parts of the combined cycle. These include improvements to the combustion turbine engine, turbine cooling, compressors, condensers, and more. Improved performance in industry standard combined cycles has resulted from years of iterative industry innovation.

The evolution of GE gas turbines offers an example of the evolution of gas turbines over time to produce more efficient technology. GE currently offers 7HA and 9HA gas turbines, which run at 60 hertz (Hz) and 50 Hz, respectively. Both turbines are “H-class” technology, which include combustion turbines with firing temperatures greater than 1,430oC. The H-class technology is the latest evolution of GE gas turbines that includes the E-class and F-class gas turbines as previous iterations. In general, the firing temperature has increased from the E-class (earliest iteration) to the H-class (latest iteration), and the resulting combined cycled efficiency has increased as well. In addition, the H-class gas turbines include entirely air-cooled hot gas paths due to advanced turbine cooling, sealing, materials, and coating. Within the 7/9HA gas turbines, the 7/9HA.01 turbines were the first iteration, and the 7/9HA.02 turbines came afterwards. The upgrade from the “.01’s” to the “.02’s” increased power output because of increased compressor inlet and turbine exit annulus areas, with an increased pressure ratio to maintain flow. It should be noted that the HA products can ramp to full plant load in less than 30 minutes, ensure ramping capability in emissions compliance of greater than 15 percent load per minute, and include fuel flexibility to operate on both gaseous and liquid fuels. It should also be noted that a third generation 7HA gas turbine, 7HA.03, has been designed are even more efficient, and the first two GE 7HA.03 gas turbines have recently began operating at the Dania Beach Clean Energy Center (DBEC) in Broward County, Florida. Combustion turbine combined cycle design specifications are outlined for the 7/9HA family in Figure 2.

Figure 2: Design Specifications at ISO Conditions for the GE 7/9 HA Gas Turbine Family

| Model | No. & Type Gas Turbine | Net Plant Output (kW) | Net Heat Rate (Btu/kWh) | Net Plant Efficiency (LHV) | Net Plant Efficiency (HHV) |
| --- | --- | --- | --- | --- | --- |
| 9HA.01 (50 Hz) | 1 x 9HA.01 | 680,000 | 5,356 | 63.7% | 57.4% |
| 9HA.01 (50 Hz) | 2 x 9HA.01 | 1,363,000 | 5,345 | 63.8% | 57.5% |
| 9HA.02 (50 Hz) | 1 x 9HA.02 | 838,000 | 5,320 | 64.1% | 57.7% |
| 9HA.02 (50 Hz) | 2 x 9HA.02 | 1,680,000 | 5,306 | 64.3% | 57.9% |
| 7HA.01 (60 Hz) | 1 x 7HA.01 | 438,000 | 5,481 | 62.3% | 56.1% |
| 7HA.01 (60 Hz) | 2 x 7HA.01 | 880,000 | 5,453 | 62.6% | 56.4% |
| 7HA.02 (60 Hz) | 1 x 7HA.02 | 573,000 | 5,381 | 63.4% | 57.1% |
| 7HA.02 (60 Hz) | 2 x 7HA.02 | 1,148,000 | 5,365 | 63.6% | 57.3% |
| 7HA.03 (60 Hz) | 1 x 7HA.03 | 640,000 | 5,342 | 63.9% | 57.6% |
| 7HA.03 (60 Hz) | 2 x 7HA.03 | 1,282,000 | 5,331 | >64.0% | >57.6% |

Notice that small increases in net plant efficiency occur by collocating two gas turbines at one combined cycle plant.

Another advanced combustion turbine operating within combined cycle class is the Siemens HL gas turbine. The “HL” terminology intends to indicate that the current technology serves as intermediate between H-class technology and the L-class technology of the future which will be capable of 65% efficiency (LHV) when employed in a combined cycle plant. The HL combustion turbine evolved from the H-class turbine with some notable improvements. Namely, the turbine inlet temperature of the HL combustion turbine is about 100oC higher than that of the H-class, which has a large impact on efficiency increase. Additionally, a new combustion system, called “Advanced Combustion system for high Efficiency” (ACE), is employed to reduce the increase in NOx emissions resulting from the inlet temperature increase. Moreover, the number of compressor stages is reduced from 13 to 12, while simultaneously increasing the pressure ratio for increased performance and reduced complexity. Turbine blade internal cooling features were added to accommodate the higher temperatures, which also reduces dependency on cooling air consumption. Lastly, internally cooled free-standing blades are employed in stage 4 of the turbine, as opposed to uncooled blades in stage 4 for the H-class turbines, resulting in both higher power output and exhaust temperatures. Exhaust temperatures of the HL-class combustion turbine at designed to be around 680oC, compared to 630oC for Siemen’s H-class combustion turbine.

Additionally, the U.S. Department of Energy’s (DOE) Advanced Turbines Program is supporting the development of advanced turbine technologies, which includes combined cycle. The program’s goal is reach 65% efficiency (LHV) for combined cycle technology by conducting research on hot section components and technology, including, but not limited to, materials, advanced cooling, leakage control, advanced aerodynamics, and altogether new turbine design concepts. Most notable, the program hopes to develop combustors to operate at higher temperatures with lower NOx emissions. More specifically, there is an aim to improve the firing temperature of combustion turbines in combined cycle plants to 3,100oF. Furthermore, it should also be noted that the DOE cited combined cycle efficiency goals of 67% (LHV) and “long-term” goals of 70% efficiency (LHV) in its 2022 fiscal year congressional budget request. Combined cycle power plants employing Siemens HL-class technology are currently rated at >63% combined cycle efficiency, compared to 61% for those plants employing H-class technology.

## HRSG Configurations

The design of an HRSG can impact how long it takes to start producing steam and generating power. Currently, the most efficient combined cycle EGUs utilize HRSGs with a steam reheat cycle and multi-pressure steam. A steam reheat cycle extracts and reheats steam that has been partially expanded in the steam turbine prior to expansion in the lower pressure portion of the turbine. A reheat module allows more efficient operation of the steam turbine and prevents formation of water droplets that can damage the steam turbine’s lower pressure stages. The use of three discrete steam pressures (high pressure (HP), intermediate pressure (IP), and low pressure (LP)) maximizes efficiency. Each of these three sections contains separate superheater, evaporator, steam drum, and economizer modules. The HP steam section is located on the high-temperature end of the HRSG, closest to the combustion turbine exhaust duct. The LP steam section is located on the low-temperature end of the HRSG, just before the stack. This arrangement maximizes the degree of superheat (i.e., the quantity of energy per pound of steam) delivered to the steam turbine. Simpler, low-cost, less-efficient HRSGs are also available in single-, double-, and triple-pressure designs and without a reheat cycle. After the energy has been extracted for steam production, the flue gas enters an economizer, which preheats the condensed feedwater recycled back to the HRSG. The final heat recovery section, which is not used on all combined cycle EGUs, is the fuel preheater. The fuel preheater, which is not used in all combined cycle EGUs, preheats the fuel used for the combustion turbine engine.

While a HRSG has no moving parts, thermal inertia and rapid heating can stress the components of the HRSG and shorten the operating life of the unit. The high-pressure drum is the most vulnerable component when subjected to rapid heating; therefore, the drum is typically heated slowly with designated hold points during startup. While relatively inefficient, a dual-pressure HRSG without a reheat cycle has a simpler startup procedure and can start quicker than a more efficient triple-pressure HRSG with a steam reheat cycle. Also, an auxiliary boiler can maintain the HRSG temperature, reducing the time required for an HRSG to begin producing steam. However, the use of an auxiliary boiler decreases the overall efficiency of the combined cycle EGU.

For HRSGs, there are currently three main configurations found in industry: 2-pressure non-reheat (2PNR), 3-pressure non-reheat (3PNR), and 3-pressure reheat (3PRH). The two-pressure (2P) versus three-pressure (3P) designations refer to the number of steam pressures in the steam cycle. 2P steam cycles employ two steam turbines—a low pressure (LP) steam turbine and a high pressure (HP) steam turbine. Similarly, 3P steam cycles employ three steam turbines, where one is an LP turbine, one is an HP turbine, and the third, located between the LP and HP turbines, is an intermediate (IP) pressure turbine. 2P and 3P cycles can also employ reheating as a method to increase steam turbine efficiency. With reheating, steam is routed back to the HRSG to be reheated prior to further expansion through subsequent lower pressure turbines.

A HRSG can also include duct burners, sometimes called supplemental firing. Supplemental firing is the mixing of additional fuel to turbine exhaust—which still contains available oxygen to support additional combustion. The combustion of this supplemental fuel increases the useful thermal output of the HRSG and is typically only done during periods of high electric demand. While the use of duct burners can increase output during critical periods, they reduce the overall efficiency of the combined cycle EGU. Since the additional fuel is only using the bottoming Rankine cycle, incremental efficiencies are on the order of a simple cycle combustion turbine. Typically duct burners are categorized as either small or large based on duct size, spacing and design constraints. Small duct burners are intended to make up capacity that is lost during period of high ambient temperatures. Small duct burners only impact efficiency while operating. In contrast, combined cycle designs with large duct burners oversize the steam turbine relative to the output that can be provided by the combustion turbine engine. The use of large duct burners provides significant additional capacity. However, since the steam turbine is more often operating at partial load and is less efficient, the combined cycle efficiency is impacted even when the duct burners are not operating.

An alternative to the use of duct burners is complementary firing. Complementary firing combines a relatively small combustion turbine(s) with a larger combined cycle facility. The small turbine is generally used during periods when the steam turbine is not operating at capacity (e.g., during periods of high ambient temperature that often correspond to periods of peak electric demand). The exhaust from the smaller turbine is sent to the HRSG of the combined cycle EGU. In essence, the smaller combustion turbine is a combined cycle EGU that is used for peaking applications. The benefits of complementary firing include that the incremental electricity is generated more efficiently than by using duct burners or from a stand-alone simple cycle turbine and the exhaust from the small combustion turbine is routed through the post combustion control technology of the larger combined cycle EGU. An additional advantage of complimentary firing compared to the use of duct burners is that since the majority of the incremental electricity is generated by the turbine engine, there is potentially less demand placed on the Rankine cycle portion of the larger combined cycle EGU. Drawbacks of complimentary firing compared to the use of duct burners are higher capital costs, less fuel flexibility (duct burners can burn a variety of fuels), and more limited part-load performance.

# Potential Efficiency Gains in the Bottoming (Rankine) Cycle

The primary differences between a 2PNR, 3PNR, and 3PRH HRSGs are efficiencies and construction costs. The complexity and cost increases with the number of steam pressures. However, increasing the number of steam pressures allows more energy to be extracted from the exhaust gas, improving overall efficiency. A reheat cycle adds additional complexity and capital costs but increases the efficiency of the Rankine cycle by increasing the average temperature of the heat addition within the process. These capital costs can at least be partially offset by reductions in fuel costs. 2P and 3P HRSG without a reheat cycle have efficiencies of approximately 20 and 26%, respectively. A 3P HRSG with a reheat cycle improves the efficiency of thermal energy to electrical output to approximately 30%.

According to Gas Turbine World, all aeroderivative and frame combined cycles with base load ratings of less than 500 MMBtu/h use 2P HRSG. 3P HRSG without a reheat cycle are used for frame combined cycle EGUs up to 2,000 MMBtu/h, and 3P HRSG with a reheat cycle are used for frame combined cycle EGUs with base load ratings of greater than 2,000 MMBtu/h. From a practical standpoint, the use of a reheat cycle is limited to combustion turbines turbine engines with exhaust temperatures greater than 593 oC and for steam turbines greater than 60 MW. However, 3P HRSG have been applied to aeroderivative combined cycle EGUs and could be adopted un smaller frame combined cycle EGUs as well.

Several studies have compared various HRSG configurations for a combined cycle EGUs. One study directly compared 2PNR, 3PNR, and 3PRH steam cycles. It concluded that increasing the number of pressure cycles leads to an increase in efficiency of the whole cycle. Additionally, the study concluded that although increasing steam generation pressure levels requires a larger upfront investment, it ultimately yields a higher return, and the net present value (NPV) of the higher-pressure level plants (i.e., 3PRH) increases. The study concluded that the estimated net-present value of a 3PNR and 3PNR plant increase by 0.03% and 7%, respectively, when compared to that of a 2PNR plant. Figure 3 shows the costs and efficiencies with more complex HRSG configurations compared to one with a 2PNR HRSG.

Figure 3: Relative Efficiencies and Costs of CC with Various HRSG Configurations

| HRSG Configuration | CC Net Efficiency | Increase in CC Efficiency Relative to 2PNR | CC Cost ($/kW) | Increase in CC Cost Relative to 2PNR |
| --- | --- | --- | --- | --- |
| 2PNR | 56.06% | - | 520.1 | - |
| 3PNR | 56.22% | 0.29% | 530.5 | 2.0% |
| 3PRH | 57.15% | 1.9% | 540.6 | 3.9% |

It should also be noted that single pressure HRSG technology is available as well. While they are the lowest cost and simplest HRSG design, they are also the least efficient and infrequently used in new combined cycle EGUs. The thermal efficiency of a single pressure, no reheat, HRSG system is estimated to be 3.7% less than that of a comparable 2PNR system. One study estimated the efficiencies and electricity costs of single, dual, and triple pressure HRSGs. It found that, when compared to single pressure HRSGs, dual pressure and triple pressure HRSGs resulted in combined cycle efficiencies increasing by 4.5% and 7.2%, respectively. Moreover, the study estimated the cost of electricity from NGCCs utilizing single pressure, dual pressure, and triple pressure HRSGs to be $48.13/MWh, $46.39/MWh, and $45.79/MWh, respectively. According to this study, utilizing a dual pressure HRSG may result in a 3.6% electricity cost reduction compared to single-pressure HRSG utilization, and utilizing a triple pressure HRSG may result in a 4.9% electricity cost reduction compared to single-pressure HRSG utilization. Figure 4 shows the costs and efficiencies with more complex configurations compared to one with a single pressure HRSG.

Figure 4: Relative Efficiencies and COE with Various HRSG Configurations

| HRSG Configuration | CC Net Efficiency | Increase in CC Efficiency Relative to 1-pressure | Total Capital Requirement (TCR) (million $) | Increase in TCR relative to 1-pressure | COE ($/MWh) | Decrease in COE Relative to 1-pressure |
| --- | --- | --- | --- | --- | --- | --- |
| 1-pressure | 50% | - | 116.1 | - | 48.13 | - |
| 2-pressure | 52.25% | 4.5% | 119.3 | 2.76% | 46.39 | 3.62% |
| 3-pressure | 53.6% | 7.2% | 129.9 | 11.89% | 45.79 | 4.86% |

## Heat Recovery Steam Generation Design Optimization

For a given HRSG design, parameters can be thermodynamically optimized to achieve the maximum overall efficiency. Optimization HRSG performance can identify a best-case scenario for which similar-designed HRSGs could be operated. Examples of design parameters include, but are not limited to, the pinch point temperature difference, inlet gas temperature, exit gas temperature, pressure within the turbine(s), mass flow rate, heat transfer area, pipe/tube/steam materials, condenser and cooling tower heat transfer surface area, steam turbine exhaust annulus area, external insulation to extract additional useful thermal output while maintaining the flue gas above the flue gas temperature, etc. Studies have both thermodynamically and economically optimized HRSG performance and development.

One study thermodynamically optimized parameters within HRSGs for single, double, and triple pressure turbine use. The results indicate that single-pressure, double-pressure, and triple-pressure HRSGs can increase combined cycle power output by 0.05, 0.28, and 0.29%, respectively, for every 10-bar inlet pressure increase. Furthermore, it found that the net combined cycle power output will decrease by 0.54, 0.21, and 0.17% for every 10oC evaporator pinch point temperature difference. The results suggest that significant performance increase can result from choosing optimum operating conditions for a given HRSG. Additionally, the findings suggest that single-pressure HRSGs are most susceptible to efficiency decrement for suboptimum operation, and triple-pressure HRSGs have the most potential for improvement through optimization.

In addition, integrated fuel gas heating results in higher turbine efficiency due to the reduced fuel flow required to raise the total gas temperature to firing temperature. Fuel heating occurs before the fuel is fed into the combustion chamber of the combustion turbine and can be carried out by using the heat of the exhaust gases of the combustion turbine. Heating fuel gas from a base temperature of 0oC to a temperature of 450oC increases combustion turbine efficiency from 35.05 to 35.39%.

## Intercooled Combined Cycle

Intercooling is a concept that is being used in the latest combustion turbine systems. In simple cycle systems, intercooling is used to improve the overall efficiency and reduce the compression work by cooling the hot gases to atmospheric temperature. The energy of the hot water at the intercooler outlet is lost to the atmosphere. In a combined cycle combustion turbine this energy could be used to heat the feed water to the HRSG. In a combined cycle plant, the feed water entering the HRSG must have a higher temperature than the dew of the acid vapor of sulfur. The application of the intercooler as the feed water heater of the HRSG increases the overall efficiency of the combined cycle as it reduces the compression work in the upper cycle. An increase of feed-water temperature from 20 to 60oC could increase the overall efficiency by around 2%.

## Blowdown Heat Recovery

In NGCC plants, the concentration of impurities in the steam flow must be controlled to prevent corrosion of the steam turbine blades. A portion of saturated water is continuously drained through boiler blowdown where it is discharged to the outside environment through a steam vent or drain flow. This process wastes energy and decreases the efficiency and net generated power of the cycle. Waste heat from the boiler blowdown stream can be recovered with a heat exchanger, a flash tank, or a combination of both. In a flash tank, the pressure can be lowered to allow a portion of the blowdown to be converted into low-pressure steam which can be used in the cycle again as a heat source to preheat the feed water. The recovery of the wasted heat contributes to an increase in net power and energy efficiency of the Rankine cycle, as well as a reduction in annual water usage. The usage of a flash tank could increase the net power and the energy efficiency of the Rankine cycle by 0.72% 0.23% respectively. Since about 1/3 of the output from a combined cycle is from the Rankine cycle, blowdown heat recovery could increase the output of the combined cycle EGU by 0.24% and the absolute efficiency by 0.077%.

## Design and Operating and Maintenance Practices

While several state-of-the-art turbines and design alterations exist for new NGCC plants to maximize efficiency, efficiency can also be gained for existing NGCC by proper maintenance and reparations/reinstallation of various working components within a NGCC. All major manufacturers offer packages for plants to uprate, and these include improvements to seals, vanes, blades, and other materials within a plant. GE currently offers improved wire brush seals which can act as an alternative to both labyrinth seals for compressor shafts and high-pressure packing seals. Replacing the labyrinth and/or high-pressure seals can result in output increases of 1% and 0.3%, respectively, and heat rate increases of 0.5% and 0.2%, respectively. Moreover, advanced materials can reduce the need to cool turbine blades, or steam cooling of turbine blades can be used to recover the steam in a closed loop. Other options resulting in improvements for the power generation process include advanced coatings of turbine blades and combustor components, replacement of combustion liners, replacement of turbine vanes/blades, and inlet-air fogging. Figure 5 outlines the capacity and heat rate impacts and the corresponding capital costs for various turbine upgrades.

Figure 5: Comparison of various turbine upgrade options

| Combustion Turbine Upgrade Option | MW Increase (%) | Heat Rate Impact (%) | Capital Cost ($/kW) |
| --- | --- | --- | --- |
| Comprehensive Upgrade | 10-20 | 1-5 | 150-250 |
| High-Flow Inlet Guide Vanes | 4.5 | 1 | <100 |
| Hot Section Coatings | 5-15 | 0.5-1 | 50-100 |
| Compressor Coatings | 0.5-3 | 0.5-3 | 50 |
| Inlet-Air Fogging | 5-15 | 1-5 | 50-100 |
| Supercharging Plus Fogging | 15-20 | 4 | 200 |

Proper cleaning of HRSG components can also have worthwhile impacts on turbine performance as it can maintain low pressure drop across the HRSG. Various contaminants, most notably ammonium bisulfate, can accumulate in the HRSG which can produce pressure losses. In one case study on HRSG cleaning, GE removed 14 tons of debris, resulting in a reduced turbine back pressure of 8 inches water column. The combined annual fuel savings and additional power output are believed to have netted the facility $500,000/year in avoided costs/additional revenue. Similarly, plant condensers should be regularly cleaned. Airborne dust and debris can regularly accumulate and degrade condenser performance. Note that turbine overhauls can range from $2-$12 million for 200 MW turbines but could provide heat rate improvements of 100-300 Btu/kWh, which represents around 1-3% of the steam cycle. Additionally, proper O&M practices can reduce heat rates by around 30-70 Btu/kWh (~0.3-0.7% of steam cycle) for cost of $30,000 annually, and feed pump rebuilds can improve the steam cycle heat rates by 0.25-0.5% for costs of $250,000-$350,000.,

As it relates to the steam system, there are several operational practices which can reduce the heat losses within the system. Some of these methods are outlined as follows:

- Minimize air-in leakage

- Clean HRSG heat transfer surfaces

- Improve water treatment to minimize HRSG blowdown

- Recover energy from HRSG blowdown

- Add/restore HRSG and steam plant insulation

- Optimize deaerator vent rate

- Repair steam leaks

- Minimize vented steam

- Ensure that steam system piping, valves, fittings, and vessels are well insulated

- Implement an effective team-trap maintenance program

- Isolate steam from unused lines

- Optimize condensate recovery

- Clean combustion turbine flow path components

## Once Through (Benson®) HRSG Technology

The use of a once-through (i.e., Benson®) HRSG can also improve the ability of a combined cycle EGU to start quickly and maintain efficiency at part load. A once-through HRSG does not have a steam drum like a more traditional HRSG. Instead, the feedwater is converted to steam in the HRSG furnace waterwalls and goes directly into the steam turbine. This allows for the use of higher-pressure steam, which improves design efficiencies, provides higher part-load efficiencies, allows reduced startup times, and results in more flexible operation.

The Benson Technology is touted as “a proven process for large-scale steam generation in power plants with the heart of this process being the once-through principle. Combined with sliding pressure operation, this allows for highly efficient, flexible, and reliable power plant operation”.

Advantages of the Benson Once-Through HRSG

- It retains all the virtues of the proven natural circulation principle of drum-type boilers (i.e. flow stability and uniform temperature distribution), yet at the same time replaces the high-pressure drum with thin-walled components to improve operating flexibility.

- Significant shortening of plant startup time by allowing unrestricted combustion turbine start-up.

- Increase of efficiency during start-up by minimizing combustion turbine operation in part loads.

- Reduction of gaseous and liquid emissions through shorter start-up process and elimination of drum blow down.

- Reduced consumption of chemicals through advanced feedwater treatment.

- Improved efficiency at high ambient temperatures due to adjustable evaporating point.

- Capability for higher steam parameters (pressure and temperature), because there are no limitations through natural circulation.

Figure 6: From Siemens “BENSON® Once-Through Heat Recovery Steam Generator” brochure, pg. 3 (2006)

## The Use of Supercritical Steam Conditions

Combined cycle EGUs typically have HRSGs that operate at subcritical steam conditions. However, once-through HRSGs can be designed to operate using supercritical steam conditions. “Supercritical” is a thermodynamic term describing the state of a substance in which there is no clear distinction between the liquid and the gaseous phase (i.e., they are a homogenous fluid). In contrast to a subcritical steam generator, a supercritical steam generator operates at pressures above the critical pressure—3,200 psi (22 MPa). Combustion turbine engines larger than approximately 200 MW typically have exhaust temperatures high enough to support the use of supercritical steam conditions. However, the steam turbine in combined cycle configurations where one turbine engine is paired with a steam turbine (1-1 configuration) is smaller than typical EGUs using supercritical steam conditions. Steam turbine sizes in combined cycle configurations where 2 or 3 large turbines are paired with a single steam turbine (2-1 or 3-1 configuration) are as large of typical EGUs using supercritical steam conditions.

Thermodynamic modeling has been applied to assess the potential of using supercritical steam as the working fluid in the HRSG. One study suggests that using a supercritical steam once-through HRSG will increase steam power by 5% when compared to using a subcritical steam HRSG. Since the steam turbine typically makes up approximately one-third of the overall output of a combined cycle EGU, if a combined cycle EGU designed to use supercritical steam conditions in the high-pressure portion of the steam turbine would reduce overall fuel use by 2 percent. Another study analyzed the improvement of a 3PRH CC EGU when using supercritical steam as opposed to subcritical steam. It indicates that if using a supercritical steam as the working fluid for the HP turbine, it is possible to get a plant efficiency of 64.45% and capacity of 1.214 GW power output, compared to 63.08% and 1.19 GW when using subcritical steam. Additionally, the economic analysis predicts that plants can return up to an additional $14 million per year when considering the difference between the annual revenue from electricity sales and annual fuel costs when using supercritical steam.

Another study compared the use of 2P and 3P cycles using subcritical and supercritical steam conditions with and without steam reheat. The results followed the patterns such that efficiency increased from 2P to 3P, from non-reheat to reheat, and from subcritical to supercritical. The analyses were conducted on a Siemens V94.3 combined cycle gas combustion turbine, and the findings are outlined in Figure 7.

Figure 7: Result of Thermodynamic Analysis of Siemens V94.3 Combined Cycle Gas Combustion Turbine Efficiencies[40]

| HRSG Cycle | HP-Pressure (bar)a | Net LHV CC Efficiency (%) | Relative CC Efficiency Increase (%) |
| --- | --- | --- | --- |
| 2PNR | 80 | 53.6 | - |
| 2PRH | 140 | 54.0 | 0.75 |
| 3PNR | 100 | 54.1 | 0.93 |
| 3PRH | 140 | 54.6 | 1.87 |
| 2PRH - Supercritical | 250 | 54.6 | 1.87 |
| 3PRH - Supercritical | 260 | 55.1 | 2.80 |

a Pressures are provided as “reasonable” choices for each HRSG cycle type

While combined cycle efficiencies routinely get above 55% on a higher heating value (HHV) basis, in current times, the result of the Bolland (1990) study still carries important implications for the comparisons of 2PNR, 3PNR, and 3PRH HRSG’s. Additionally, it useful to compare the three HRSG types with subcritical and supercritical steam as the working fluid. As shown in Figure 3 the use of supercritical steam appears to be an important option in increasing efficiency, with the efficiency of a dual pressure supercritical reheat HRSG being equal to that of a triple pressure reheat.

## The Use of Alternate Working Fluid

In addition, alternate working fluids—such as the use of organic fluids, supercritical CO2 (sCO2), or ammonia/water mixtures rather than steam—also have the potential to increase the efficiency of combined cycle EGUs. Organic Rankine cycles are primarily applicable to temperatures lower than combustion turbine engine exhaust temperatures. While the use of sCO2 as the working fluid in a Rankine cycle is of most interest for nuclear and coal-fired EGUs, it also has the potential to improve the overall efficiency of combined cycle EGUs. The primary efficiency benefit would be for combined cycle EGUs using smaller frame or aeroderivative combustion turbine engines that typically use a double-pressure HRSG without a reheat cycle. However, a HRSG using sCO2 has the potential to improve the efficiency of combined cycle EGUs compared to triple-pressure steam with a reheat cycle as well.

The potential of sCO2 has been assessed in multiple studies. One study found sCO2 potentially has more compact, lower-cost exhaust heat exchanger (EHX) technology when comparing system cost and performance of sCO2 to steam-based combined cycle, the sCO2 cycles generated higher power output at a lower cost than steam systems. Additionally, when including operation and maintenance costs (O&M), calculations demonstrated that sCO2 can provide levelized cost of electricity (LCOE) advantages as well. When comparing different steam turbine models, the LCOE decreased by an average of 15% when using sCO2 versus subcritical steam. Another study modeled the performance of sCO2 steam use versus 2PNR and 3PRH alternative HRSG use. It found that when compared to steam for bottom cycles for 2PNR, sCO2 as a working fluid has significantly reduced exergy flow losses at pressures above 200 bar, resulting in better performance. However, when compared to 3PRH, assuming high sCO2 expander and pump isentropic efficiencies at 95%, the maximum pressure of the sCO2 cycle needs to exceed 300 bar to outperform 3PRH steam cycles.

DOE’s National Energy Technology Laboratory (NETL) is working on improvements to a sCO2 power cycle. One pilot power plant was recently completed which uses sCO2 technology. In 2018, Southwest Research started building a Supercritical Transformational Electric Power (STEP) pilot plant, which will use sCO2 technology with a design capacity of 10 MWe. It is estimated that replacing water with sCO2 increases the efficiency by up to 10%. Additionally, STEP turbomachinery can be 1/10th the size of a conventional power plant components, providing potential to lower environmental footprint and construction costs of new facilities. NETL conducted a study on the use of sCO2 in coal-fired power plants that indicate a sCO2 power cycle can achieve higher efficiencies than a pulverized coal (PC)/Rankine systems using supercritical steam conditions with no increase of cost of electricity.

Another report, released by Echogen, compared the use of sCO2 as the Rankine Cycle working fluid to that of a steam-based Rankine Cycle system. Echogen claims their EPS100 has up to 40% lower install cost per kilowatt than that of a comparable dual pressure steam system utilizing GT-PRO/PEACE. The install cost largely results from the smaller installation footprint and simplicity of the sCO2 system. The lower install costs contribute to a 10 to 20% lower levelized cost of electricity of the EPS100 system compared to that of traditional dual pressure heat recovery steam generators. In Canada, Siemens Energy and TC Energy agreed to build a waste-heat-to-power facility using the EPS100 technology. Commissioned in 2022, the facility captures waste heat from a combustion turbine and converts it into power using a sCO2 power cycle.

Ammonia/water mixtures can be utilized as a working fluid through the Kalina Cycle. Depending on the application, the Kalina Cycle can improve power plant efficiency by 10 to 50 percent over the Rankine Cycle. As plant operating temperatures are lowered, the Kalina Cycle experiences a higher increase in relative gain in comparison to the Rankine Cycle. Advantages for the Kalina Cycle include lower upfront capital costs, lower demand for cooling water and cooling infrastructure, minimal maintenance downtime, and minimal required supervision. A study found that the use of ammonia water instead of a steam only cycle increased the efficiency of the system from 57.5 percent to 62.5 percent, while the cost of electricity marginally increased from $0.06718/kWh to $0.06723/kWh. A study on a system with intercooling, a triple-pressure reheat HRSG, and ammonia/water cycle at each pressure level produced a minimum cost of electricity production of 0.06723 $/kWh. The same system obtained a 62.5 percent maximum value of efficiency, a second law efficiency of 60.7 percent, and a maximum work output of 1789.39 kJ/kg of air.

## The Use of Thermoelectric Materials

Combined cycle EGUs generate significant quantities of relatively low-temperature heat (i.e., waste or byproduct heat) that cannot be used by the traditional Rankine cycle and is sent to the power plant cooling system (i.e., cooling tower). If this energy could be recovered to produce additional electricity, it could reduce the environmental impact of power generation. Thermoelectric materials (e.g., bismuth telluride (Bi2Te3), lead telluride (PbTe), silicon-germanium (SiGe, magnesium antimonide (Mg3Sb2), and magnesium bismuthide (Mg3Bi2)) can be used to generate electricity due to temperature differences across the material., While still in development, this technology has the potential to recover useful energy from the waste heat from power plants. However, if a thermoelectric generator were able to convert 5 percent of combustion turbine waste heat to electric output, the CO2 emissions rate for simple cycle EGUs would be reduced by approximately 10 percent and combined cycle EGUs by approximately 5 percent.

Currently, optimizing thermo electric generation (TEG) power output and efficiency very dependent on thermoelectric (TE) material properties and dimensions. Currently, TE materials are based on use of tellurium and germanium, which are expensive elements. Consequently, development of polymer, silicide, oxide and tetrahedrite TE materials are being explored. Challenges of commercial TEG are mainly the materials development and systems engineering.

However, the potential of TEG utility has been studied and shown promising results. On a study of a ship’s waste heat recovery, it was concluded that a TEG-organic Rankine cycle (ORC) method increase waste heat utilization rate while reducing power generation cost. Results show that for a TEG/ORC bottom cycle ratio of 0.615, the output power, thermal efficiency, and generation cost of the TEG-ORC combined cycle experimental system were estimated to be 134.50 W, 6.93%, and 0.461 $/kWh, respectively. Another study showed the promise of bismuth-telluride-based thermoelectric micro-generators (μ-TEGs) when it found that a power output of 5.5 μW per thermocouple can be generated under a temperature difference of only 5 K. The findings of these studies are indicative of TEGs potential to increase energy efficiency of combustion turbines.

## Combined Cycle Start-up Times

Improving start-up time of combined cycle EGUs make combined cycle EGUs a more dependable power source for load following supply, and research/practice suggests several ways to improve combined cycle start-up times. Combustion turbines operating as EGUs in a combined cycle system have historically been designed to operate for extended periods of time at steady loads. Since these combined cycle EGUs were not intended to start and stop on a regular basis, they had relatively long startup times depending on unit-specific factors and whether startup was initiated from a cold, warm, or hot state. During the past decade, the demands placed on this conventional mode of steady, base-load operation have changed. The latest combined cycle EGUs are designed with advanced technology and features to be more flexible and respond faster to increased demand for reliable electricity, support increased generation from intermittent sources (i.e., renewables), capitalize on financial incentives to improve dispatch or supply non-spinning reserves, operate at higher efficiencies, and emit less pollution. As a result, advanced fast-start, combined cycle EGUs incorporate multiple techniques that allow the EGU to start and stop faster, cycle output faster, and maintain higher part-load efficiencies than previous designs.

Several combustion turbine manufacturers market complete combined cycle systems that can ramp up to full load from a cold start in less than an hour, depending on unit-specific factors. Advanced combustion turbines, when isolated from the HRSG and steam turbine, can reach full load at full speed as a simple cycle (i.e., Brayton) unit in less than 20 minutes. When adhering to some of the following fast-start techniques, the HRSG, steam turbine, and balance of plant equipment can reach safe operating temperatures and pressures and begin generating additional electricity within 30-45 minutes of ignition of the combustion turbine. Techniques that can be used to reduce start-up times for combined cycle systems are discussed below.

Slower start up time of combined cycle EGUs is largely attributed HRSG’s needing a slower and more gradual start-up to reduce thermal stress in the HRSG thick-walled components, such as steam drums. During start-up, a temperature gradient will exist between the inside and outside of a steam drum, leading damage of the steam drum if not properly managed. However, because the slow start-up of the full combined cycle is limited by the HRSG, the combustion turbine can start-up and begin producing power if the combustion turbine exhaust gas is properly managed.

One option is to employ a bypass damper to reduce the amount of exhaust gas passing through the HRSG as it warms up. The damper blocks the natural draft of cooler, ambient air back through the HRSG stack. Another practice to maintain temperature is to insulate the HRSG stack. Keeping critical elements of the HRSG in a warm or hot state following shutdown is an important technique for reducing startup times. Reducing the exhaust gas passing through the HRSG allows for the steam turbine to ramp up to full power without jeopardizing the thick-walled components within the HRSG.

Additionally, bypass stack allows the exhaust energy from the combustion turbine to be decoupled from the heat recovery unit and steam turbine generator. The bypass allows the combustion turbine engine—the fastest-starting component of a combined cycle system—to operate independent of the HRSG and come to partial or full load as a simple cycle EGU at a faster ramp rate. Documented start times range from approximately 10 minutes for a hot start to approximately 15-20 minutes for a warm start and to approximately 20-25 minutes for a cold start. The HRSG, steam turbine generator, and balance of plant piping and equipment can then be slowly brought to temperature while the combustion turbine engine operates at high load.  The use of preheaters to gradually warm major steam lines can add significant time to startup procedures. Figure 4 compares the load path and hot start time of a conventional combined cycle combustion turbine to that of an advanced class fast-start unit.

During a conventional startup, combined cycle turbines hold at low load for an extended time to gradually warm the HRSG and steam turbine generator components and prevent thermal stresses that can reduce the lifespan of the equipment.67 The elimination of this long hold is key to a fast start and may be possible with a bypass stack and a modulated damper that can control the amount of exhaust heat and flow that control the steam production rate and temperatures that reach the HRSG. Fast-start, advanced class combined cycle designs may include a HRSG capable of tolerating rapid changes in temperature and flow of high-temperature exhaust generated by rapidly ramping the turbine.67

Additionally, the start-up time of an HRSG is largely dependent on how warm the system is already (i.e., warm start vs. cold start). Maintaining warm conditions for the HRSG after shut-down can result in faster start-up times when ramping back up. One option to do this is with cascaded latent heat storage (CLHS), which can deploy stored thermal energy to keep HRSG warm. Note that start-up times to reach full load can be significantly faster for hot start-ups compared to cold start-ups. One estimate indicates that the duration of start-up for cold, warm, and hot combined cycle plants average around 147.5, 117.5, and 50 minutes, respectively. Thus, there is incentive to keep HRSG warm when feasible.

## Purge Credit

This technique involves an EGU receiving credit for a mandatory purging of the fuel systems during shutdown and adding isolation valves in the fuel supply system. This purge of residual fuel from the combustion system with fresh, ambient air is necessary to remove excess combustible fuels in the unit and lower the risk of fire. During a conventional combined cycle startup, this purge takes place prior to ignition, which increases start times, reduces efficiency by decreasing the temperature of the HRSG, and increases thermal fatigue on the units. Generating purge credits during shutdown allows fast-start EGUs to start up without a purge.

Appendix

Emissions Data

Introduction

This appendix describes the approach used by the EPA to identify the best performing combustion turbines with respect to efficient generation.

Approach to Identify the Best Performing Base Load and Intermediate Load Combustion Turbines

To determine the 12-operating month emissions rate (lb CO2/MWh-gross) that is equivalent to the best system of emission reduction (BSER), the EPA analyzed the reporting CO2 emissions per megawatt hour of gross generation reported by owners/operators of combustion turbines to the EPA’s Clean Air Markets Division (CAMD). The EPA reviewed monthly emissions data between 2014 and 2021 for all simple and combined cycle combustion turbines that reported CEMS emissions data to EPA’s CAMD’s emissions collection and monitoring plan system (ECMPS). The procedure EPA used to determine the best performing units is as follows:

- 12-operating month average emission rates were determined using reported monthly data from January 2014 to December 2021

- The combustion turbines were sorted by lowest maximum 12-operating month emissions rate

  - The EPA filtered out combined heat and power combustion turbines

- The best performing/most efficient combustion turbines (combustion turbines with the lowest maximum emissions rate) were sorted into two groups: simple and combined cycle combustion turbines

  - The EPA used the maximum emissions rate and not the average or lowest achieved emissions rate because 111(b) emission standards are never to be exceeded standards and this approach takes into account variability in identifying the best performing combustion turbines

- The EPA determined the 12-operating month intermediate load emission rates by only considering average 12-operating month capacity factors of greater than 20% on a heat input basis

  - For simple cycle turbines with no intermediate data, the EPA substituted in the highest low load 12-operaitng month average as representative of intermediate load operation—the EPA did this to avoid missing the best performing simple cycle turbines if they never operated as an intermediate load combustion turbine

- The EPA determined the 12-operating month base load emissions rate by only considering average 12-operating month capacity factors of greater than 50% on a heat input basis

  - The EPA only considered emission rates from combustion turbines with over 12 12-operating month emission rates—this requires a minimum of 24 months of operation as a base load combustion turbine and assures variability is taken into account

Simple Cycle Turbines with the Lowest Reported Intermediate Loas Emission Rates

Based on the maximum reported intermediate load 12-operating month emission rates (with substituted low load emission rates for combustion turbines that haven’t operated as intermediate load combustion turbines), 53 simple cycle turbines have maintained annual emission rates of 1,150 lb CO2/MWh-gross, 15 have maintained annual emission rates of 1,100 lb CO2/MWh-gross, and 2 have maintained 12-operating month emission rates of 1,000 lb CO2/MWh-gross. Figure 1 shows the reported emission rates.

Figure 1: 12-Operating Month Intermediate Load Emission Rates for the Best Performing Simple Cycle Turbines

| Facility Name | Facility ID (ORISPL) | Unit ID | Commercial Operation Date | Hourly Heat Input (MMBtu/h) | Max 12-Operating Month Intermediate Load Emissions Rate (lb CO2/MWh-gross) | Turbine Model | Frame or Aeroderivative |
| --- | --- | --- | --- | --- | --- | --- | --- |
| NCPA Combustion Turbine Project #2 | 7449 | NA1 | 04/01/96 | 463 | 983 | General Electric Co-LM5000-PD (STIG) | Aeroderivative |
| Redding Power Plant | 7307 | 6 | 11/12/10 | 508 | 998 |  |  |
| Panoche Energy Center | 56803 | 1 | 04/09/09 | 975 | 1,049 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Woodland Generation Station | 7266 | 1 | 12/03/93 | 460 | 1,050 | General Electric Co-LM5000-PD (STIG) | Aeroderivative |
| Panoche Energy Center | 56803 | 4 | 04/17/09 | 974 | 1,064 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Washington Parish Energy Center | 55486 | CTG02 | 10/01/20 | 2,201 | 1,074 | General Electric 7FA | Frame |
| Scattergood Generating Station | 404 | 7 | 09/14/15 | 903 | 1,077 | General Electric Co-LMS100PA-SAC (Water) | Aeroderivative |
| Panoche Energy Center | 56803 | 3 | 04/13/09 | 955 | 1,077 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Cumberland Energy Center | 5083 | 05001 | 05/07/09 | 1,150 | 1,080 | General Electric Co-LMS100PA-SAC (Steam) | Aeroderivative |
| Walnut Creek Energy Park | 57515 | GT1 | 12/31/12 | 892 | 1,080 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Panoche Energy Center | 56803 | 2 | 04/18/09 | 970 | 1,082 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Washington Parish Energy Center | 55486 | CTG01 | 09/19/20 | 2,201 | 1,089 | General Electric 7FA | Frame |
| Haynes Generating Station | 400 | 13 | 02/17/13 | 907 | 1,092 | General Electric Co-LMS100 | Aeroderivative |
| Walnut Creek Energy Park | 57515 | GT3 | 02/09/13 | 892 | 1,098 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Walnut Creek Energy Park | 57515 | GT2 | 01/12/13 | 892 | 1,098 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Haynes Generating Station | 400 | 15 | 05/14/13 | 907 | 1,103 | General Electric Co-LMS100 | Aeroderivative |
| Haynes Generating Station | 400 | 11 | 04/14/13 | 907 | 1,104 | General Electric Co-LMS100 | Aeroderivative |
| Victoria Port Peaking Facility | 61242 | CT1 | 03/25/19 | 473 | 1,105 | General Electric LM6000 | Aeroderivative |
| Haynes Generating Station | 400 | 14 | 03/05/13 | 907 | 1,114 | General Electric Co-LMS100 | Aeroderivative |
| Groton Generating Station | 56238 | CT002 | 07/01/08 | 787 | 1,114 | General Electric Co-LMS100PA-SAC (Water) | Aeroderivative |
| Haynes Generating Station | 400 | 16 | 04/18/13 | 907 | 1,115 | General Electric Co-LMS100 | Aeroderivative |
| Pueblo Airport Generating Station | 56998 | CT08 | 11/28/16 | 375 | 1,119 | General Electric LM 6000 PF | Aeroderivative |
| Almond Power Plant | 7315 | 1 | 04/08/96 | 459 | 1,119 | General Electric Co-GE LM6000 | Aeroderivative |
| Walnut Creek Energy Park | 57515 | GT4 | 02/09/13 | 892 | 1,120 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Haynes Generating Station | 400 | 12 | 04/13/13 | 907 | 1,120 | General Electric Co-LMS100 | Aeroderivative |
| Walnut Creek Energy Park | 57515 | GT5 | 03/08/13 | 892 | 1,120 | General Electric Co-LMS100PB-DLE2 | Aeroderivative |
| Clayville | 58235 | U1 | 11/01/15 | 628 | 1,120 | Rolls Royce Corp-Trent 60 | Aeroderivative |
| Bayonne Energy Center | 56964 | GT7 | 03/25/12 | 603 | 1,124 | Rolls Royce Corp Trent 60 WLE ISI | Aeroderivative |
| Sowega Power Project | 7768 | CT2 | 06/28/99 | 614 | 1,128 | General Electric Co-GE LM6000 |  |
| Victoria City Peaking Facility | 61241 | CT1 | 12/17/19 | 473 | 1,128 | General Electric Co-LM6000PC Sprint | Aeroderivative |
| Aurora | 55279 | AGS07 | 04/26/01 | 510 | 1,128 | General Electric Co-MS6001FA |  |
| Ocotillo Power Plant | 116 | GT6 | 02/15/19 | 1,000 | 1,130 | General Electric LMS100 | Aeroderivative |
| Bayonne Energy Center | 56964 | GT1 | 01/23/12 | 603 | 1,131 | Rolls Royce Corp Trent 60 WLE ISI | Aeroderivative |
| Ocotillo Power Plant | 116 | GT5 | 03/13/19 | 1,000 | 1,131 | General Electric LMS100 | Aeroderivative |
| Victoria City Peaking Facility | 61241 | CT2 | 12/17/19 | 473 | 1,134 | General Electric Co-LM6000PC Sprint | Aeroderivative |
| Bayonne Energy Center | 56964 | GT2 | 01/26/12 | 603 | 1,135 | Rolls Royce Corp Trent 60 WLE ISI | Aeroderivative |
| Bayonne Energy Center | 56964 | GT8 | 04/11/12 | 603 | 1,135 | Rolls Royce Corp Trent 60 WLE ISI | Aeroderivative |
| Pinckneyville Power Plant | 55202 | CT03 | 06/15/00 | 444 | 1,137 | General Electric Co-Unknown |  |
| Howard M Down | 2434 | U11 | 04/05/12 | 610 | 1,137 | Rolls Royce Corp-Trent 60 | Aeroderivative |
| Bayonne Energy Center | 56964 | GT5 | 03/13/12 | 603 | 1,139 | Rolls Royce Corp Trent 60 WLE ISI | Aeroderivative |
| Ocotillo Power Plant | 116 | GT3 | 04/06/19 | 1,000 | 1,139 | General Electric LMS100 | Aeroderivative |
| Pio Pico Energy Center LLC | 57555 | CTG3 | 07/03/16 | 1,000 | 1,142 | General Electric Co-LMS100PA-SAC (Water) | Aeroderivative |
| Scattergood Generating Station | 404 | 6 | 08/09/15 | 903 | 1,143 | General Electric Co-LMS100PA-SAC (Water) | Aeroderivative |
| Ocotillo Power Plant | 116 | GT7 | 01/16/19 | 1,000 | 1,144 | General Electric LMS100 | Aeroderivative |
| Shelby County | 55237 | SCE4 | 07/01/00 | 444 | 1,146 | General Electric Co-LM6000PC |  |
| Pinckneyville Power Plant | 55202 | CT02 | 06/06/00 | 444 | 1,146 | General Electric Co-Unknown |  |
| Aurora | 55279 | AGS05 | 04/21/01 | 510 | 1,146 | General Electric Co-MS6001FA |  |
| Kearny Generating Station | 2404 | 133 | 05/09/12 | 490 | 1,148 | General Electric Co-LM6000PC | Aeroderivative |
| Antelope Elk Energy Center | 57865 | 2 | 04/14/16 | 1,941 | 1,148 | GE 7F.05 | Frame |
| Antelope Elk Energy Center | 57865 | 1 | 05/21/15 | 1,941 | 1,149 | GE 7F.05 | Frame |
| Sand Hill Energy Center | 7900 | SH3 | 03/01/01 | 478 | 1,149 | General Electric Co-LM6000PC |  |
| Shelby County | 55237 | SCE5 | 07/01/00 | 444 | 1,149 | General Electric Co-LM6000PC |  |
| Pio Pico Energy Center LLC | 57555 | CTG2 | 07/22/16 | 1,000 | 1,150 | General Electric Co-LMS100PA-SAC (Water) | Aeroderivative |
| Shelby County | 55237 | SCE7 | 01/01/01 | 444 | 1,152 | General Electric Co-LM6000PC |  |
| Sand Hill Energy Center | 7900 | SH4 | 03/01/01 | 478 | 1,153 | General Electric Co-LM6000PC |  |
| Malaga Power | 56239 | GT-2 | 06/01/05 | 480 | 1,154 | General Electric Co-LM6000PC Sprint | Aeroderivative |

Combined Cycle Turbines with the Lowest Reported Base Load Emission Rates

Based on the maximum reported base load 12-operating month emission rates, 1 combined cycle facility with 3 separate combustion turbine engines has maintained annual emission rates of 730 lb CO2/MWh-gross, 17 individual combustion turbine engines have maintained annual emission rates of 770 lb CO2/MWh-gross, and 62 have maintained 12-operating month emission rates of 800 lb CO2/MWh-gross. Figure 2 shows the reported for the best performing base load combustion turbines.

Figure 2: 12-Operating Month Base Load Emission Rates for the Best Performing Combustion Turbines

| Facility Name | Facility ID (ORISPL) | Commercial Operation Date | Capacity Input (MMBtu/h) | Maximum 12-Operating Month Base Load Emissions Rate (lb CO2/MWh-gross) |
| --- | --- | --- | --- | --- |
| Okeechobee Clean Energy Center | 60345 | 10/10/2018 | 3,096 | 717 |
| Okeechobee Clean Energy Center | 60345 | 10/30/2018 | 3,096 | 719 |
| Okeechobee Clean Energy Center | 60345 | 9/23/2018 | 3,096 | 722 |
| Greensville County Power Station | 59913 | 8/11/2018 | 4,500 | 740 |
| Port Everglades | 617 | 7/31/2015 | 2,648 | 750 |
| CPV Fairview, LLC | 60589 | 9/22/2019 | 3,763 | 754 |
| CPV Fairview, LLC | 60589 | 9/27/2019 | 3,763 | 754 |
| Port Everglades | 617 | 7/21/2015 | 2,648 | 755 |
| Port Everglades | 617 | 11/7/2015 | 2,648 | 758 |
| IPL - Eagle Valley Generating Station | 991 | 11/13/2017 | 2,542 | 761 |
| Woodbridge Energy Center | 57839 | 10/25/2015 | 2,807 | 761 |
| Dresden Energy Facility | 55350 | 10/27/2011 | 2,250 | 762 |
| Bridgeport Harbor Station | 568 | 5/9/2019 | 3,706 | 765 |
| Lagoon Creek | 7845 | 6/30/2010 | 2,243 | 765 |
| IPL - Eagle Valley Generating Station | 991 | 11/1/2017 | 2,542 | 765 |
| Dresden Energy Facility | 55350 | 11/8/2011 | 2,250 | 767 |
| Pasadena Power Plant | 55047 | 7/1/2000 | 1,980 | 769 |
| Riviera Beach Energy Center | 619 | 10/8/2013 | 3,046 | 773 |
| Woodbridge Energy Center | 57839 | 11/4/2015 | 2,807 | 774 |
| Greensville County Power Station | 59913 | 7/20/2018 | 4,500 | 775 |
| Lackawanna Energy Center | 60357 | 9/12/2018 | 3,500 | 780 |
| Riviera Beach Energy Center | 619 | 9/22/2013 | 3,046 | 780 |
| Lackawanna Energy Center | 60357 | 7/1/2018 | 3,304 | 780 |
| Lackawanna Energy Center | 60357 | 3/3/2018 | 3,304 | 782 |
| Magic Valley Generating Station | 55123 | 7/29/2001 | 2,700 | 782 |
| Cape Canaveral | 609 | 11/23/2012 | 3,046 | 783 |
| Birdsboro Power | 61035 | 2/7/2019 | 3,345 | 784 |
| Allen | 3393 | 9/20/2017 | 3,797 | 784 |
| Kendall Green Energy LLC | 1595 | 8/8/2002 | 2,450 | 784 |
| Oregon Clean Energy Center | 59764 | 3/8/2017 | 3,237 | 785 |
| Riviera Beach Energy Center | 619 | 10/30/2013 | 3,046 | 785 |
| Cape Canaveral | 609 | 12/16/2012 | 3,046 | 786 |
| Cape Canaveral | 609 | 12/6/2012 | 3,046 | 786 |
| Colorado Bend II | 60122 | 3/2/2017 | 4,564 | 787 |
| Wolf Hollow II | 59812 | 1/5/2017 | 4,564 | 788 |
| Greensville County Power Station | 59913 | 7/30/2018 | 4,500 | 789 |
| Colorado Bend II | 60122 | 2/10/2017 | 4,564 | 790 |
| St. Joseph Energy Center LLC | 57794 | 12/29/2017 | 2,636 | 791 |
| St. Joseph Energy Center LLC | 57794 | 12/17/2017 | 2,636 | 792 |
| Oregon Clean Energy Center | 59764 | 5/18/2017 | 3,237 | 792 |
| Moxie Freedom Generation Plant | 59906 | 2/7/2018 | 3,700 | 792 |
| Crystal River | 628 | 10/16/2018 | 3,292 | 793 |
| Crystal River | 628 | 8/27/2018 | 3,292 | 793 |
| Rio Nogales Power Project, LP | 55137 | 4/1/2002 | 2,090 | 793 |
| Sewaren Generating Station | 2411 | 4/27/2018 | 4,182 | 793 |
| Crystal River | 628 | 8/23/2018 | 3,292 | 794 |
| CPV Towantic Energy Center | 56047 | 2/26/2018 | 2,899 | 794 |
| Crystal River | 628 | 10/7/2018 | 3,292 | 794 |
| Wolf Hollow II | 59812 | 1/12/2017 | 4,564 | 794 |
| CPV Towantic Energy Center | 56047 | 1/27/2018 | 2,899 | 794 |
| Moxie Freedom Generation Plant | 59906 | 3/11/2018 | 3,700 | 794 |
| Polk | 7242 | 2/23/2007 | 2,215 | 795 |
| Newark Energy Center | 58079 | 3/22/2015 | 2,531 | 795 |
| West County Energy Center | 56407 | 9/9/2009 | 2,958 | 795 |
| Clean Energy Future - Lordstown, LLC | 60376 | 7/14/2018 | 3,630 | 796 |
| Martin | 6043 | 12/10/2004 | 2,306 | 797 |
| Plant H. Allen Franklin | 7710 | 12/8/2001 | 2,600 | 797 |
| Newark Energy Center | 58079 | 3/9/2015 | 2,531 | 798 |
| ExxonMobil Beaumont Refinery | 50625 | 3/10/2005 | 2,531 | 799 |
| Rio Nogales Power Project, LP | 55137 | 4/1/2002 | 2,105 | 799 |
| Polk | 7242 | 4/24/2002 | 2,215 | 800 |
| Martin | 6043 | 12/15/2004 | 2,306 | 800 |
| West County Energy Center | 56407 | 12/3/2010 | 3,098 | 801 |
| West County Energy Center | 56407 | 12/18/2010 | 3,098 | 801 |
| Hamilton Liberty Generation Plant | 58420 | 1/6/2016 | 3,144 | 802 |
| West County Energy Center | 56407 | 4/19/2009 | 2,958 | 802 |
| Polk | 7242 | 4/2/2007 | 2,215 | 802 |
| West County Energy Center | 56407 | 9/2/2009 | 2,958 | 802 |
| West County Energy Center | 56407 | 9/24/2009 | 2,958 | 802 |
| Caithness Long Island Energy Center | 56234 | 4/17/2009 | 2,650 | 803 |
| Clean Energy Future - Lordstown, LLC | 60376 | 7/13/2018 | 3,630 | 803 |
| Fox Energy Center | 56031 | 4/28/2005 | 2,587 | 803 |
| Wansley CC (55965) | 55965 | 12/13/2001 | 2,350 | 803 |
| Hamilton Liberty Generation Plant | 58420 | 2/4/2016 | 3,144 | 803 |

The EPA also evaluated the maximum 12-operating month emission rates of simple cycle and combined cycle turbines and compared the emission standards the EPA is considering for emission standards that are representative of a BSER based on efficient generation in combination with best operating and maintenance practices. The EPA added additional best performing combustion turbines that commenced construction prior to 2015. Figures 3 and 4 show the proposed standards relative to the performance of combustion turbines that have commenced operation since 2015.

Combined cycle EGUs using dry cooling or simple cycle EGUs do not have water eco-system impacts.

https://www.ge.com/gas-power/resources/education/combined-cycle-power-plants

GTW (2021). 2021 GTW Handbook. Volume 36. Page 79. Pequot.

United States Environmental Protection Agency (EPA) (2022). Available and Emerging Technologies for Reducing Greenhouse Gas Emissions from Combustion Turbine Electric Generating Units. EPA Office of Air and Radiation. April 21, 2022. Accessed at https://www.epa.gov/system/files/documents/2022-04/epa_ghg-controls-for-combustion-turbine-egus_draft-april-2022.pdf

Meher-Homji, C., Mee, T. (2000). Gas Turbine Power Augmentation by Fogging of Inlet Air. Proceedings of the 28th turbomachinery Symposium (2000), Texas A&M. Accessed at https://oaktrust.library.tamu.edu/bitstream/handle/1969.1/163382/Vol28010.pdf?sequence=1&isAllowed=y.

Savic, S., Hemminger, B., Mee, T. (2013). High Fogging Application for Alstom Gas Turbines. Proceedings of PowerGen. November 2013. Accessed at http://www.meefog.com/wp-content/uploads/High-Fogging-Alsotom-Mee_-2013-2.pdf.

GE (n.d.) SPRINT * SPray INTercooling for power augmentation. Accessed at https://www.ge.com/gas-power/services/gas-turbines/upgrades/sprint.

EPA (2002). CAM Technical Guidance Document. B.17 Water or Steam Injection. Accessed at https://www3.epa.gov/ttnchie1/mkb/documents/B_17a.pdf.

Kotob, M. R., Lu, T., Wahid, S. S. (2021). Experimental comparison between steam and water tilt-angle injection effects on NOx reduction from the gaseous flame. Royal Society of Chemistry. 10.1039/D1RA03541J

Bouam, A., Aissani, S., Kadi, R. (2019). Gas Turbine Performances Improvement using Steam Injection in the Combustion Chamber under Sahara Conditions. Oil and Gas Science and Technology. Institut Français du Pétrole (IFP), 2008, 63 (2), pp.251-261. 10.2516/ogst:2007076ff. ffhal-02001998f

Wang, F. J., Chiou, J. S. (2002). Performance improvement for a simple cycle gas turbine GENSET – a retrofitting example. Applied Thermal Engineering 22 (2002) 1105-1115. Accessed at https://citeseerx.ist.psu.edu/viewdoc/download?doi=10.1.1.583.9680&rep=rep1&type=pdf.

GE Power & Water. Accessed at https://www.ge-distributedpower.com/products/power-generation/15-to-35-mw/lm2500-stig/.

Bahrami, S., et al (2015). Performance Comparison between Steam Injected Gas Turbine and Combined Cycle during Frequency Drops. Energies 2015, Volume 8. https://doi.org/10.3390/en8087582.

Mitsubishi Power. Smart-AHAT (Advanced Humid Air Turbine. Accessed at https://power.mhi.com/products/gasturbines/technology/smart-ahat.

Ganapathy, V., Heil, B., Rentz, J. (1988). Heat Recovery Steam Generator for Cheng Cycle Application. Industrial Power Conference, PWR, Vol. 4. Accessed at http://v_ganapathy.tripod.com/cheng.pdf.

Digumarthi, R., Chang, C. (1984). Cheng-Cycle Implementation on a Small Gas Turbine Engine. Journal of Engineering for Gas Turbines and Power. Volume 106, Issue 3. https://doi.org/10.1115/1.3239626.

DOE NETL. Pressure Gain Combustion. Accessed at https://netl.doe.gov/node/7553.

DOE (2016). Combined Cycle Power Generation Employing Pressure Gain Combustion. Accessed at https://www.osti.gov/servlets/purl/1356814.

Neumann, Nicolai, & Peitsch, Deiter (2019). Potentials for Pressure Gain Combustion in Advanced Gas Turbine Cycles. Accessed at https://www.mdpi.com/2076-3417/9/16/3211.

Vandervort, C., Leach, D., Scholz, M. (2016). Advancements in H Class Gas Turbines for Combined Cycle Power Plants for High Efficiency, Enhanced Operational Capability, and Broad Fuel Flexibility.8th International Gas Turbine Conference. 12-13 Oct. 2016. Brussels, Belgium. https://etn.global/wp-content/uploads/2018/09/ADVANCEMENTS-IN-H-CLASS-GAS-TURBINES-FOR-COMBINED-CYCLE-POWER-PLANTS-FOR-HIGH-EFFICIENCY-ENHANCED-OPERATIONAL-CAPABILITY-AND-BROAD-FUEL-FLEXIBILITY.pdf.

Patel, S. (2022). GE Debuts First 7HA.03 Gas Turbines at 1.3-GW Plant in Florida. Power Magazine. Accessed at https://www.powermag.com/ge-debuts-first-7ha-03-gas-turbines-at-1-3-gw-plant-in-florida/

GTW (2021). 2021 GTW Handbook. Volume 36. Page 82-90. Pequot.

Modern Power Systems (2018). Siemens HL: the bridge to 65%+ efficiency. Accessed at https://www.modernpowersystems.com/features/featuresiemens-hl-the-bridge-to-65-efficiency-6045386/.

U.S. Department of Energy (DOE) (2021). Advanced Turbines. Accessed at https://netl.doe.gov/sites/default/files/2021-10/Program-108.pdf.

DOE National Energy Technology Laboratory (NETL). Advanced Combustion Turbines. Accessed at https://netl.doe.gov/carbon-management/turbines/act.

Efficiency using LHV for combined cycles using natural gas.

DOE (2022). Department of Energy FY 2022 Congressional Budget Request. DOE/CF-0174, Volume 3 Part 2, Page. 199. Accessed at https://www.energy.gov/sites/default/files/2021-06/doe-fy2022-budget-volume-3.2_0.pdf.

Gas Turbine World (2021). 2021 GTW Handbook. Volume 36. Page 82-90. Pequot.

Pasha, A. (1992). Combined Cycle Power Plant Start-up Effects and Constraints of the HRSG. Proceedings of ASME Turbo Expo, 1992. Power of Land, Sea, and Air. https://doi.org/10.1115/92-GT-376.

Pasha, A. (1992). Combined Cycle Power Plant Start-up Effects and Constraints of the HRSG. Proceedings of ASME Turbo Expo, 1992. Power of Land, Sea, and Air. https://doi.org/10.1115/92-GT-376.

The complimentary fired combustion turbine engines would be sized such that the turbine exhaust could be accommodated by the HRSG. This generally limits the size of the complimentary turbine engine(s) to less than 10% of the output of the primary turbine engine(s).

In order to achieve part-load capabilities with complimentary firing multiple smaller turbines would be required.

GTW (2021). 2021 GTW Handbook. Volume 36. Pages 27-28. Pequot.

Rashidi, M. M., Aghagoli, A., Ali, M., Thermodynamic Analysis of a Steam Power Plant with Double Reheat and Feed Water Heaters. Advances in Mechanical Engineering. Volume 2014, Article ID 940818, 11 pages. https://doi.org/10.1155%2F2014%2F940818

Chase, D.L. and P.T. Kehoe, GE Combined-Cycle Product Line and Performance. GE Power Systems. GER-3574G

https://www.ijert.org/off-design-performance-analysis-of-a-triple-pressure-reheat-heat-recovery-steam-generator

Mansouri, M. T., Ahmadi, P., Kaviri, A. G., Jaafar, M. N. M. (June 2012). Exergetic and economic evaluation of the effect of HRSG configurations on the performance of combined cycle power plants. Energy Conversion and Management. Volume 58. Pages 47-58. https://doi.org/10.1016/j.enconman.2011.12.020.

Chase, D.L. and P.T. Kehoe, GE Combined-Cycle Product Line and Performance. GE Power Systems. GER-3574G

Zhao, Y., Chen, H., Waters, M., Mavris, D. N. (2003). Modeling and Cost Optimization of Combined Cycle Heat Recovery Generator Systems. Proceedings of ASME Turbo Expo, 2003. Power of Land, Sea, and Air. https://doi.org/10.1115/GT2003-38568.

Rahim, M. A. (September 2012). Combined Cycle Power Plant Performance Analyses Based on the Single-Pressure and Multipressure Heat Recovery Steam Generator. Journal Of Energy Engineering. Volume 138, Issue 3. https://doi.org/10.1061/(ASCE)EY.1943-7897.0000063

Marin, G. et al. (2020). Study of the effect of fuel temperature on gas turbine performance. Accessed at https://www.e3s-conferences.org/articles/e3sconf/abs/2020/38/e3sconf_hsted2020_01033/e3sconf_hsted2020_01033.html.

Shukla, P., et al (2010). A Heat Recovery Study: Application of Intercooler As A Feed-Water Heater of Heat Recovery Steam Generator. Accessed at https://asmedigitalcollection.asme.org/IMECE/proceedings-abstract/IMECE2010/44298/611/357134.

Saedi, Ali, et al (2022). Feasibility study and 3E analysis of blowdown heat recovery in a combined cycle power plant for utilization in Organic Rankine Cycle and greenhouse heating. Accessed at https://www.sciencedirect.com/science/article/pii/S0360544222019600.

DOE (2012). Recover Heat from Boiler Blowdown. https://www.energy.gov/eere/amo/articles/recover-heat-boiler-blowdown#:~:text=Heat%20can%20be%20recovered%20from,occur%20with%20high%2Dpressure%20boilers.

Vandani, Amin, et al (2015). Exergy analysis and evolutionary optimization of boiler blowdown heat

recovery in steam power plants. Accessed at https://www.sciencedirect.com/science/article/pii/S0196890415008535.

Andover Technology Partners (2018). Improving Heat Rate on Combined Cycle Power Plants. Accessed at https://www.andovertechnology.com/wp-content/uploads/2021/03/C_18_EDF_FINAL.pdf.

Andover Technology Partners (2018). Improving Heat Rate on Combined Cycle Power Plants. Accessed at https://www.andovertechnology.com/wp-content/uploads/2021/03/C_18_EDF_FINAL.pdf.

Costs shown in 2002 dollars.

May include “replacement of combustion liners, transition pieces, 1st stage turbine vanes, and 2nd stage vanes and blades with [GE] Frame 7EA parts.”

GE (2017). When is 28,000 pound pile of rust a good thing?. Accessed at https://www.ge.com/content/dam/gepower-new/global/en_US/downloads/gas-new-site/services/hrsg-services/pressurewave-case-study.pdf.

Andover Technology Partners (2018). Improving Heat Rate on Combined Cycle Power Plants. Accessed at https://www.andovertechnology.com/wp-content/uploads/2021/03/C_18_EDF_FINAL.pdf.

Costs given in 2008 dollars.

Sargent & Lundy (2009). Coal-Fired Power Plant Heat Rate Reductions. SL-009597. Final Report. Accessed at https://www.epa.gov/sites/default/files/2015-08/documents/coalfired.pdf.

Andover Technology Partners (2018). Improving Heat Rate on Combined Cycle Power Plants. Accessed at https://www.andovertechnology.com/wp-content/uploads/2021/03/C_18_EDF_FINAL.pdf.

https://www.siemens-energy.com/global/en/offerings/power-generation/power-plants/benson-technology.html ; https://assets.siemens-energy.com/siemens/assets/api/uuid:b5c2c3b8-eb59-430b-8065-ba09d31eb37b/flyer-benson-hrsg-210920.pdf ; and https://assets.siemens-energy.com/siemens/assets/api/uuid:ef5fb27a-d2e0-4222-a0d0-2cd24146a937/new-benson-evaporator.pdf

https://www.siemens-energy.com/global/en/offerings/power-generation/power-plants/benson-technology.html ; https://assets.siemens-energy.com/siemens/assets/api/uuid:b5c2c3b8-eb59-430b-8065-ba09d31eb37b/flyer-benson-hrsg-210920.pdf ; and https://assets.siemens-energy.com/siemens/assets/api/uuid:ef5fb27a-d2e0-4222-a0d0-2cd24146a937/new-benson-evaporator.pdf

Alobaid, Falah & Ströhle, Jochen & Epple, Bernd & Kim, Hyun-Gee (2009). Dynamic simulation of a supercritical once-through heat recovery steam generator during load changes and start-up procedures. Applied Energy, Elsevier, vol. 86(7-8), pages 1274-1282, July. https://ideas.repec.org/a/eee/appene/v86y2009i7-8p1274-1282.html.

Marcin Jamróz, Marian Piwowarski, Paweł Ziemia´nski, and Gabriel Pawlak (2021). Technical and Economic Analysis of the Supercritical Combined Gas-Steam Cycle. Energies 2021, 14, 2985. https://www.mdpi.com/1996-1073/14/11/2985

Bolland, Olav (1990). A Comparative Evaluation of Advanced Combined Cycle Alternatives. American Society of Mechanical Engineers (ASME). https://doi.org/10.1115/90-GT-335.

The Kalina Cycle® is another cycle that has the potential for efficiency gains compared to a water-based Rankine cycle. See http://www.kalinapower.com/technology/.

Patel, S. (2021b, October 27). The POWER interview: Pioneering STEP supercritical carbon dioxide demonstration ready for 2022 commissioning. Power. https://www.powermag.com/the-power-interview-pioneering-step-supercritical-carbon-dioxide-demonstration-readying-for-2022-commissioning/?oly_enc_id=3025B2625790F2W

Using the design HRSG efficiencies listed in Gas Turbine World and the efficiency of the design efficiency of the Echogen supercritical EPS100 heat recovery system (24 percent net, https://www.echogen.com/our-solution/product-series/eps100/), the median decrease in design heat rates for replacing dual pressure HRSG with supercritical CO2 HRSG is 7 percent.

Thanganadar, D., Asfand, F., & Patchigolla, K. (2019). Thermal performance and economic analysis of supercritical carbon dioxide cycles in combined cycle power plant. Applied Energy, 255(1), 113836. https://doi.org/10.1016/j.apenergy.2019.113836

Levelized cost of electricity (LCOE) is defined as the price at which the generated electricity should be sold for the system to break even at the end of its lifetime. LCOE is a good indicator of cost-effectiveness, because it can be calculated without requiring for assumptions about the price at which the electricity can be sold to the grid or to an end user, as is the case when calculating the payback period or the net present value. LCOE is an indicator that can be used to compare different technologies, without any framework conditions affecting the assessment. With the use of LCOE, the financial viability in specific conditions can be indicated by just comparing directly the LCOE with the price at which electricity could be sold. Papapetrou M., Kosmadakis G. (2022). Salinity Gradient Heat Engines, https://www.sciencedirect.com/topics/engineering/levelized-cost-of-electricity

Held, T (2015). Supercritical CO2 for Gas Turbine Combined Cycle Power Plants. Echogen Power Systems. Power Gen International, December 8-10, Las Vegas, Nevada. https://www.echogen.com/_CE/pagecontent/Documents/Papers/Supercritical%20CO2%20Cycles%20for%20Gas%20Turbine%20Combined%20Cycle%20Power%20Plants.pdf.

Huck, Pierre, Freund, Sebastian, Lehar, Matthew, & Peter, Maxwell (2016, March 28-31). Performance comparison of supercritical CO2 versus steam bottoming cycles for gas turbine combined cycle applications. GE Global Research. The 5th International Symposium - Supercritical CO2 Power Cycles, http://sco2symposium.com/papers2016/SystemConcepts/092paper.pdf

https://netl.doe.gov/project-information?p=FE0028979

https://www.swri.org/press-release/step-10-megawatt-supercritical-carbon-dioxide-pilot-plant-building

Southwest Research Institute (SRI) (2022). Supercritical Transformational Electric Power Pilot Plant. https://www.swri.org/industry/advanced-power-systems/supercritical-transformational-electric-power-pilot-plant.

NETL (2019). Supercritical Carbon Dioxide (Sco2) Cycle As An Efficiency Improvement Opportunity For Air-Fired Coal Combustion. Accessed at https://www.osti.gov/servlets/purl/1511695.

Persichilli, M., Kacludis, A., Zdankiewicz, E., Held, T. (April 2012). Supercritical CO2 Power Cycle Developments and Commercialization: Why sCO2 can Displace Steam. Echogen Power Systems LLC. Accessed at https://www.echogen.com/_CE/pagecontent/Documents/Papers/why-sco2-can-displace-steam.pdf.

Power Magazine (2021). First Commercial Deployment of Supercritical CO2 Power Cycle Taking Shape in Alberta. Accessed at https://www.powermag.com/first-commercial-deployment-of-supercritical-co2-power-cycle-taking-shape-in-alberta/.

Kaline Power (2015). Technology: Kalina Cycle. Accessed at http://www.kalinapower.com/technology/.

Maheshwari, M., Singh, O. (2020). Thermo-economic analysis of combined cycle configurations with intercooling and reheating. Accessed at https://www.sciencedirect.com/science/article/pii/S0360544220311567.

Electricity can also be generated from electrochemical reactions at different temperatures and pressures, See https://jtecenergy.com/technology/. In addition, thermogalvanic cells use temperature differences to generate an electric current. (See e.g., Yuan)

Yuan Yang, et al. (2014). Charging-free electrochemical system for harvesting low grade thermal energy. https://www.pnas.org/content/111/48/17011

LeBlanc, S. (2014). Thermoelectric generators: Linking material properties and systems engineering for waste heat recover applications. Sustainable Materials and Technologies. Volumes 1-2, Pages 25-35. https://doi.org/10.1016/j.susmat.2014.11.002.

Kiu, C., Ye, W., Li, H., Liu, J., Zhao, C., Mao, Z., & Pan, X. (2020). Experimental study on cascade utilization of ship’s waste heat based on TEG-ORC combined cycle. International Journal of Energy Research. https://doi.org/10.1002/er.6083.

Oualid, S. E., Kosior, F., Dauscher, A., Candolfi, C., Span, G., Mehmedovic, E., Paris, J., & Lenoir, B. (2020). Innovative design of bismuth-telluride-based thermoelectric micro-generators with high output power. Energy & Environmental Science. Issue 10. https://pubs.rsc.org/en/content/articlelanding/2020/EE/D0EE02579H .

Gálen, S.C. (2013). Gas Turbine Combined Cycle Fast Start: The Physics Behind the Concept. Accessed at http://www.mcilvainecompany.com/Decision_Tree/subscriber/Tree/DescriptionTextLinks/Physics.pdf.

Power Magazine (2013). Fast-Start HRSG Life-Cycle Optimization. June 1, 2013. Accessed at https://www.powermag.com/fast-start-hrsg-life-cycle optimization/#:~:text=The%20temperature%20gradient%20that%20exists,pressure)%20to%20cause%20fatigue%20damage.

Eddington, et al. (2017). Fast start combined cycles: how fast is fast?. Accessed at https://www.power-eng.com/emissions/fast-start-combined-cycles-how-fast-is-fast/#gref.

Kim, T. S., Lee, D. K., Ro, S. T. (2000). Analysis of thermal stress evolution in the steam drum during start-up of a heat recovery steam generator. Applied Thermal Engineering. https://doi.org/10.1016/S1359-4311(99)00081-2.

Pasha, A. (1992). Combined Cycle Power Plant Start-up Effects and Constraints of the HRSG. Proceedings of ASME Turbo Expo, 1992. Power of Land, Sea, and Air. https://doi.org/10.1115/92-GT-376.

GE (2016). Startup time reduction for Combined Cycle Power Plants. Accessed at https://etn.global/wp-content/uploads/2018/09/Startup_time_reduction_for_Combined_Cycle_Power_Plants.pdf.

Previous combined cycle designs had to operate the combustion turbine engine at low loads to slowly increase the HRSG temperature. Configurations with a stack bypass can slowly increase the percentage of the combustion turbine engine exhaust into the HRSG to increase the HRSG temperature without damage.

Eddington, et al. (2017). Fast start combined cycles: how fast is fast?. Accessed at https://www.power-eng.com/emissions/fast-start-combined-cycles-how-fast-is-fast/#gref.

Gálen, S.C. (2013). Gas Turbine Combined Cycle Fast Start: The Physics Behind the Concept. Accessed at http://www.mcilvainecompany.com/Decision_Tree/subscriber/Tree/DescriptionTextLinks/Physics.pdf.

Li, D., Hu, Y., Li, D., Wang, J. (2019). Combined-cycle gas turbine power plant integration with cascaded latent heat thermal storage for fast dynamic responses. Energy Conversion and Management. https://doi.org/10.1016/j.enconman.2018.12.082.

Decoussemaeker, P., Nagasayanam, A., Bauver, W. P., Rigoni, L., Cinquegrani, L., Epis, G., Donghi, M. (2016). Startup Time Reduction for Combined Cycle Power Plants. The Future of Gas Turbine Technology. 8th International Gas Turbine Conference. Accessed at https://etn.global/wp-content/uploads/2018/09/STARTUP-TIME-REDUCTION-FOR-COMBINED-CYCLE-POWER-PLANTS.pdf.